## FAS
BILLS OF QUANTITIES
PROJECT :NATIONAL LAW SCHOOL OF INDIA UNIVERSITY, BENGALURU
LOCATION: BENGALURU
DESCRIPTION : PUBLIC ADDRESS SYSTEM
SL NO | DESCRIPTION | UNIT | QTY. | RATE | AMOUNT | REMARKS
1 | Supply, Installation, Testing & Commissioning of Microprocessor based 05 loops, Networkable Analogue Addressable type fire alarm control panel with Display and Fully functional QWERTY type keypad. The panel shall be equipped with 20% spare capacity with each loop having a maximum loading of 159 detectors and 159 devices in one loop. Four access levels, capable of taking Flash Scan devices, flash EPROM sufficient numbers of programmable relay controls for controlling LT Panels, Access Control Panels, AHUs, pressurization fans, ventilation fans at fire pump room, monitoring of fire sprinkler and fire hydrant pump, 240 volts AC power supply, automatic battery charger, 24 volts sealed lead acid batteries sufficient for 24 hours normal working and then be capable of operating the system for 2 hours during an emergency conditions as required. (UL 9th Edition Approved). The panel should have network cards for networking with other FACP's.The Panel Should have Dedicated Power Supply Unit for Sounders.
b) 05 - Loop panel with 3 loop cards. MAKE:NOTIFIER (PART No. : NFS2-3030D with NCM-W)
| CPU2-3030D | Nos. | 1
| SBB-C4 | Nos. | 1
| ADDR-C4 | Nos. | 1
| CA-2 | Nos. | 1
| DPA-2B | Nos. | 1
| CMIC-1 | Nos. | 1
| BP2-4 | Nos. | 1
| AMPS-24E | Nos. | 1
| CHS-4L | Nos. | 1
| DP-DISP | Nos | 1
| BMP-1 | Nos. | 2
| DP-1B | Nos. | 1
| LCM-320 | Nos | 1
| LEM-320 | Nos | 1
| DVC-EM | Nos | 1
| DVC-KD | Nos. | 1
| NCM-W | Nos. | 2
| Installation | Nos. | 1
2 | Supply and Installation of 12V 18Ah batteries
| Supply | Nos | 2
| Installation | Nos | 2
3 | Supply, Installation, Testing and commissioning of BACnet module for integration of maximum of 1 nos FACP with BMS system. Make; Notifier(PART No-HON-CGW-MBB+ NCM-W)
| Supply | Nos | 1
| Installation | Nos | 1
4 | Supply, Installation, Testing & Commissioning of Notifier Network Gateway card for creating the Notifier network and putting the FACP network on TCP/IP for local and remote monitoring and controlling from the Fire Command Center and Centralized Monitoring Centre. MAKE:NOTIFIER (PART No. : NFN-GW-EM-3 with NCM-W) Note : Client Should provide static IP
| Supply | Nos | 0
| Installation | Nos | 0
5 | SMOKE DETECTOR :
Supply, Installation, Testing & Commissioning of Acclimate Plus Photo Thermal Smoke detector with standard mounting base, Hard Address MAKE:NOTIFIER
| Supply | Nos. | 326
| Installation | Nos. | 326
6 | DUCT SENSOR
Supply, Installation, Testing & Commissioning of Addressable Duct Detector with UL listed housing and sampling tube. MAKE:NOTIFIER (PART No. : DNR + FSP-951 + DST1.5)
| Supply | Nos | RO
| Installation | Nos | RO
7 | RESPONSE INDICATOR:
Supply, Installation, Testing & Commissioning of LED type Response indicator.
| Supply | Nos. | 0
| Installation | Nos. | 0
8 | STROBE WITH SOUNDER
Supply, Installation, Testing & Commissioning of Strobe Lights Cum Hooter with 110 cd. The strobes shall be synchronized for better evacuation.MAKE:NOTIFIER (SYS-HS)
| Supply | Nos. | 12
| Installation | Nos. | 12
9 | POWER SUPPLY FOR STROBE SOUNDER
Supply , Installation,testing and commissioning of Power supply for strobe with sounder
| Supply | Nos | 12
| Installation | Nos | 12
10 | MANUAL CALL POINT:
Supply, Installation, Testing & Commissioning of Manual Call Point MAKE:NOTIFIER (PART No. F/MCP/GLASS)
| Supply | Nos. | 12
| Installation | Nos. | 12
11 | FAULT ISOLATOR MODULE:
Supply, Installation, Testing & Commissioning of Fault Isolator Module MAKE:NOTIFIER (PART No. : ISO-X)
| Supply | Nos. | 14
| Installation | Nos. | 14
12 | CONTROL MODULE:
Supply, Installation, testing and commissioning of Analogue addressable control module having rotary , decimal addressing system and shall be capable of providing DPDT contact rated 24VDC, 2A. Make: Notifier( PART NO-FCM-1)
| Supply | Nos | 8
| Installation | Nos | 8
13 | RELAY MODULE:
Supply, Installation, Testing & Commissioning of Addressable Control Relay Module, Hard Address Switch from 01-159. MAKE:NOTIFIER (PART No. : FRM-1)
| Supply | Nos. | 2
| Installation | Nos. | 2
14 | MONITOR MODULE:
Supply, Installation, Testing & Commissioning of Addressable Monitor Module, Hard Address Switch from 01-159. MAKE:Notifier(PART NO-FMM-1)
| Supply | Nos | 0
| Installation | Nos | 0
15 | HEAT DETECTOR
Supply, Installation, Testing & Commissioning of Thermal Sensor with standard mounting base, Hard Address Switch from 01-159. MAKE:NOTIFIER (PART No. : FST-951R with B-501/WHITE)
| Supply | Nos. | 0
| Installation | Nos. | 0
16 | The GUI based main network software
Supply, Installation, Testing & Commissioning of The GUI based main network software must be capable of graphically representing each facility being monitored with floor plans and icons depicting the actual locations of the various systems; and / or sensors’ locations. The GUI software shall be located in control room in one of the blocks and shall monitor all the blocks panel connected with each other. The software shall be capable of monitoring 100 Nodes with more than 20 MB baud Transmission rate on Fiber Optics Network and 10 MB baud Transmission on cable or more. The software shall provide the facility to Monitor, Control all the Digital PAVA as well as 2 way communication from main control room using voice signals over Fire Network along with the Fire detection signal. MAKE:NOTIFIER (PART No. : SW-OW-CON)
| Supply | Nos | 0
| Installation | Nos | 0
17 | Supply and Installation of 2 core 1.5 Sqmm FRLS copper armored cable with all accessories, for detctors,MCP's and all devices. (All cables should be ISI certified marked). Color: RED
| Supply | Mtrs. | 1500
| Installation | Mtrs. | 1500
18 | Supplying, drawing, connecting, testing & commissioning of 2core, 1.5 sq. mm. stranded copper conductor, pvc insulated PVC sheathed,aluminium myler tape shielded FRLS wire in existing conduit for sounder power.(all cables should be ISI marked)
| Supply | Mtrs. | 500
| Installation | Mtrs. | 500
CONDUITS & JUNCTION BOXES
19 | Supply and Installation of Octagonal shape GI Powder coated Junction box with Two glands for Fire Alarm Detector mounted on Cable Tray / Surface of Slab
| Supply | Nos. | 326
| Installation | Nos. | 326
20 | Supply and Installation of GI 3 Module metal box for Control module,Fault Isolator Module,Monitor Module, Relay Module ,Sounders,MCP Etc
| Supply | Nos. | 48
| Installation | Nos. | 48
21 | Supply and Installation of 20 mm FRLS PVC conduit-2mm thick including all accessories like bend, collar etc. for fire MCP/HTR drops. Make : Atul/VIP/Precision
| Supply | Mtrs. | 1500
| Installation | Mtrs. | 1500
TOTAL OF FAS SYSTEM |  |  |  |  | 0

## PAS
BILLS OF QUANTITIES
PROJECT :NATIONAL LAW SCHOOL OF INDIA UNIVERSITY, BENGALURU
LOCATION: BENGALURU
DESCRIPTION : PUBLIC ADDRESS SYSTEM
SL NO | DESCRIPTION | UNIT | QTY | RATE | AMOUNT | REMARKS
1 | Supplying, installing, testing and commissioning Digital Audio Amplifier designed for audio networks of up to Required DAA amplifiers terminating at a DVC Digital Voice Command. Each DAA shall be capable of accessing and processing one of up to Required audio channels on the DVC audio loop, amplifying the signal, and distributing it via four Class B or two Class A outputs at 50 watts. DAA-50 amplifiers can store backup alarm and trouble messages, and provide an adjustable background music input. An optional Firefighter's telephone riser on each DAA amplifier shall supports FFT communications riser. MAKE:NOTIFIER (PART No. : DAA2-5070E+CHS-BH1)
| Supply | Nos. | 1
| Installation | Nos. | 1
2 | Supply & installation of EQ 'D' SIZE cabinet for housing 4 No.of Amplifier. Make: Notifier(Part Code: EQBB-D4+EQDR-D4)
| Supply | Nos. | 1
| Installation | Nos. | 1
3 | Supplying, installing, testing and commissioning of Remote microphone with Zone selector in a proper housing to mount zone selector and mic. MAKE:NOTIFIER (PART No. : RM-1 with ACM-24AT+ CAB-RM)
| Supply | Nos. | 0
| Installation | Nos. | 0
4 | Supplying, installing, testing and commissioning of 2 W ceiling mounted type UL listed speakers with multi-tapping capable to produce minimum sound level of 75db at 3m distance. MAKE:NOTIFIER (PART No. : NF-SP100CI/UL) Note : Colour as per Approval
| Supply | Nos. | 268
| Installation | Nos. | 268
6 | Back box for ceiling mounted speakers
| Supply | Nos. | 268
| Installation | Nos. | 268
7 | Supply and installation of 2C x 1.5 Sqmm FRLS copper twisted shielded cable for Public address system.
| Supply | Rmt. | 200
| Installation | Rmt. | 200
8 | Supply and Installation of 25mm dia PVC FRLS Conduit - 2mm thick including all accessories like bend,collar etc.
| Supply | Rmt | 200
| Installation | Rmt | 200
9 | Supply and installation of 20mm PVC flexible conduit
| Supply | Rmt | 268
| Installation | Rmt | 268
0
TOTAL OF PUBLIC ADDRES SYSTEM |  |  |  |  | 0

## TBS
BILLS OF QUANTITIES
PROJECT :NATIONAL LAW SCHOOL OF INDIA UNIVERSITY, BENGALURU
LOCATION: BENGALURU
DESCRIPTION : TALK BACK SPEAKER SYSTEM
SL NO. | DESCRIPTION | UNIT | QTY | RATE | AMOUNT | REMARKS
1 | Supply, Unloading, Storing, Shifting to work place, Installation, testing & commissioning of 15 zone selector P.A. console and with CRCA sheet housing and control desk( rack) as required. Console shall have all call / call back facility complete with battery back up and it should also work on AC single phase power. PA console, amplifier and all associate accessories shall be installed in metal sheet fabricated cabinet ( cabinet shall be measured separately ( For Two way talk back systems ).The exisiting panel to be rechecked. The exisiting panelto be rechecked and opt for the installation. | Nos | 1
a | The system should comprises the follwing features .
b | Feather type key pads to select the zones.
c | Moulded type plastic attractive enclosure
d | Backlight liquid crystal display (LCD)
e | User friendly interactive display
f | Announcement selector - PTT Switch
g | Listen selector switch.
h | All Call swich to select all zones simultaneously for announcement
i | Zones call display on the LCD with audio alarm.
2 | Supply, Unloading, Storing, Shifting to work place, Installation, testing & commissioning of Control unit with the follwing features with all associate accessories etc complete ( For Two way talk back systems ) | Nos | 1
a | Builtin power supply
b | Zone selector switching circuit
c | Terminal blocks to terminate the zone wires , amplifier wires etc.,
d | Zone call processing circuite
3 | Supply, Unloading, Storing, Shifting to work place, Installation, testing & commissioning of approved make Goose neck Microphone with all associate accessories etc complete ( For Two way talk back systems ) | Nos | 1
4 | Supplying, installing, testing and commissioning of 6 Watts wall mounted 2-Way Talk Back speaker with press to talk switch,in CRCA sheet fabricated with LMT for talk back facility with necessary fittings etc complete.
| Supply | Nos | 12
| Installation | Nos | 12
5 | Supplying, installing, testing and commissioning of Amplifier of 250 W RMS out put including necessory control wires, jocks etc as required.
| Supply | Nos | 1
| Installation | Nos | 1
6 | Supply and installation of 2C x 1.5 Sqmm FRLS copper twisted shielded cable for talk back system.Make: Varsha/Deepanjan
| Supply | Mtrs | 500
| Installation | Mtrs | 500
7 | Supply and Installation of 25mm dia PVC FRLS Conduit - 2mm thick including all accessories like bend,collar etc.
| Supply | Mtrs | 500
| Installation | Mtrs | 500
TOTAL OF TALK BACK SYSTEM

## Breakup (hidden)
CLIENT: INFOSYS LTD | [7 empty] | #REF!
CONSULTANT: SOBHA LTD
#REF!
SUBJECT: BREAK UP
SL. NO | DESCRIPTION | FLOOR WISE QTY. | [5 empty] | TOTAL | TOTAL
|  | GF 39 (Proposed) | 1F 38 &39 (Proposed) | 2F 38 &39 (Proposed) | 3F 38 &39 (Proposed) | GF 38 (Existing) | TF | Actual | 34-35
A | Addressable Fire Alarm system
1 | Multi sensor detector(Above False ceiling) | 74 | 125 | 129 | 129 | 55 |  | 512 | 496
2 | Multi sensor detector(Below False ceiling) | 71 | 121 | 125 | 125 | 54 |  | 496 | 434
3 | Response Indicator | 71 | 121 | 125 | 125 | 54 |  | 496 | 434
4 | Below False Floor detector | 1 | 0 | 0 | 0 | 0 |  | 1 | 2
5 | Manual call point | 14 | 18 | 18 | 18 | 8 | 3 | 79 | 78
6 | Strobe with Sounder | 14 | 18 | 18 | 18 | 8 | 3 | 79 | 78
7 | Monitor module | 0 | 0 | 0 | 0 | 0 |  | 0 | 5
8 | Fault Isolator Module | 8 | 13 | 14 | 14 | 6 |  | 55 | 49
9 | Control Module (FOR HOOTER) | 3 | 5 | 5 | 5 | 2 | 1 | 21 | 20
10 | Control Module (FOR PA) | 2 | 2 | 2 | 2 | 2 |  | 10 | 10
12 | Relay Module (FOR ACCESS CONTROL SYSTEM) | 1 | 1 | 1 | 1 | 0 |  | 4 | 8
13 | Beam Detector (Transmitter) | 0 | 1 | 0 | 0 | 0 |  | 1 | 4
14 | Beam Detector (Receiver) | 0 | 1 | 0 | 0 | 0 |  | 1 | 4
15 | Modbus interface module | [6 empty] | 0 | 0
16 | NFN Card | [6 empty] | 0 | 0
17 | Fire alarm control panel (6 Loop) | [6 empty] | 0 | 0
18 | DVC | [6 empty] | 0 | 0
19 | COMBO BOX | 2 | 3 | 3 | 3 | 1 | 3 | 15 | 15
20 | DAA2-5070E | [6 empty] | 0 | 0
21 | 1.5sqmm X 2 core copper FRLS cable (Detector) | 608 | 1034.5 | 1068.5 | 1068.5 | 460.5 |  | 4664 | 3600
22 | 1.5sqmm X 2 core copper FRLS FLEXIBLE cable (CM POWER SUPPLY CABLE) | 150 | 225 | 225 | 225 | 100 |  | 1017.5 | 1000
23 | 1.5sqmm X 2 core copper Flexible cable(Sounder) | 125 | 200 | 200 | 200 | 100 |  | 907.5 | 900
24 | 20mm FRLSPVC conduits for CM & Sounder Loop | 100 | 150 | 150 | 150 | 50 |  | 660 | 660
25 | GI Junction Box for Detectors mounted on surface of the slab | 74 | 125 | 129 | 129 | 55 |  | 512 | 328
B | Public Addressable System
1 | PA speaker(Staircase) | 2 | 3 | 3 | 3 | 1 | 3 | 15 | 15
2 | Ceiling mounted PA speaker(2W)- Recess Mounted | 25 | 37 | 37 | 39 | 16 |  | 154 | 166
3 | Ceiling mounted PA speaker(2W)- Surface Mounted | 0 | 0 | 0 | 0 | 0 |  | 0 | 9
4 | Wall mounted PA speaker | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
5 | 1.5sqmm X 2 core copper flexible cable - PA Speaker | 375 | 555 | 555 | 585 | 240 |  | 2541 | 2150
6 | 20mm FRLS PVC conduits for PA Speaker | 60 | 100 | 100 | 100 | 50 |  | 451 | 450
7 | 1.5sqmm X 2 core copper flexible cable - PA Speaker(vertical riser) | 50 | 100 | 100 | 100 | 50 |  | 440 | 400