## SUMMARY
Project | : NATIONAL LAW SCHOOL OF INDIA UNIVERSITY, BENGALURU
Consultants | : LEAD CONSULTANCY & ENGINEERING SERVICES (INDIA) PVT. LTD
Subject | : SUMMARY FOR HT EXTERNAL ELECTRICAL WORKS
Rev No | : R1
Date | 06.03.2025
SL.NO. | WORK DESCRIPTION | SUPPLY AMOUNT (IN INR) | INSTALLATION AMOUNT (IN INR)
1 | SECTION I - HT WORKS | 0 | 0
2 | SECTION II - LT PANELS | 0 | 0
| AMOUNT IN INR FOR SUPPLY & INSTALLATION | 0 | 0
| TOTAL AMOUNT IN INR | 0
| GST @ 18% | 0
| GRAND TOTAL AMOUNT INCLUSIVE GST | 0
Note :
Exclusion / Assumptions :
1 | Cost of bring power to the premises.
2 | Statutory deposits & service charges.
3 | Any reworks for existing power supply line is not considered.
4 | Landscape lighting are not part of this tender same shall be in landscape scope of works

## SECTION I-HT WORKS
PROJECT | : NATIONAL LAW SCHOOL OF INDIA UNIVERSITY, BENGALURU
CONSULTANTS | : LEAD CONSULTANCY & ENGINEERING SERVICES (INDIA) PVT. LTD
SUBJECT | : SUMMARY FOR HT WORKS
REV NO | : R1
DATE | 06.03.2025
GENERAL NOTES
Note 1 | All materials & work shall be as per standards, EB and Inspectorate rules & local practice.
Note 2 | Colour conduits should be used for Data, Raw power, UPS & access control per listed below coding. (Same to verified by Electrical Contractor with Client before execution).
a) | Data - Gray
b) | Raw Power and Lighting - BLACK
c) | UPS - BLACK
d) | Fire Alarm - Red
e) | CCTV, Access Control - White
Note 3 | Vendor shall refer technical details .
Note 4 | Vendor shall follow the below colour coding for Modular Switches & Sockets.
a) | Raw Power Switches & Sockets - Front Plate shall be of white colour & Modular Power Receptacle shall be of White colour.
b) | UPS Power Switches & Sockets - Front Plate shall be of white colour & Modular Power Receptacle shall be of Black colour .
Sl No | Description | Unit | Quantity | RATE (IN INR) |  | AMOUNT (IN INR) |  | Amount
|  |  |  | SUPPLY | INSTALLATION | SUPPLY | INSTALLATION
I | EXTERNAL HT WORKS
1 | SECTION I : TRANSFORMER
1.1 | Supply, Installation, testing and commissioning of 500 kVA capacity transformer (5 star rated with energy efficiency level as per BESCOM) with 11000V primary and 433V secondary, 3phase, 50Hz, Dyn11, step down, ONAN, OLTC, Oil type, copper wound as specified with cable box on L.T side and bushing on H.T. Side and also initial fill of the oil. The rate shall include the lifting of transformer, necessary hardware, grouting etc, as required. Transformer shall meet requirements specified in the Technical specefication and losses as per IS1180 Level 2 | No. | 1 |  |  | 0 | 0
1.2 | Removing, Transporting, Handover to client, Storing of 250 kVA capacity transformer (5 star rated with energy efficiency level as per BESCOM) with 11000V primary and 433V secondary, 3phase, 50Hz, Dyn11, step down, ONAN, OLTC, Oil type, copper wound as specified with cable box on L.T side and bushing on H.T. Side and also initial fill of the oil. The rate shall include the lifting of transformer, necessary hardware, grouting etc, as required. | No. | 1 |  |  | 0 | 0
| SUB TOTAL |  |  |  |  | 0 | 0
2 | SECTION II : HT CABLE 11000V grade, END TERMINATION
Removing the End terminations for 11 KV XLPE cable.
2.01 | End Termination | Nos | 1 |  |  | 0 | 0
2.02 | Refixing the End terminations for 11 KV XLPE cable. |  |  |  |  | 0 | 0
| End Termination | Nos | 1 |  |  | 0 | 0
LT CABLES
Supply, laying, end termination, testing and commissioning of following sizes of 1100V Steel/Aluminium and Wire/Strip armoured, unarmoured, sheathed Aluminium / Copper conductor cables of approved make. End termination of cables using brass type cable glands single / double compression with aluminium / copper lugs.
Note : a) Hydraulic crimping tool shall be used for making the end terminations. b) Single compression glands - up to 150 sq.mm. c) Double compression glands for sizes > 150 sq.mm shall be used. d) Cable identification shall be made vide details furnished in single line viz., AYFY for PVC insulated, steel strip armoured, aluminium conductor cable and with PVC outer sheath.
2.03 | 3.5C x 300 Sq.mm Aluminium XLPE Armoured Cable. | Rmt | 150 |  |  | 0 | 0
| End Termination | Nos | 14 |  |  | 0 | 0
2.04 | 3.5C x 240 Sq.mm Aluminium XLPE Armoured Cable. | Rmt | RO
| End Termination | Nos | RO
2.05 | 3.5C x 185 Sq.mm Aluminium XLPE Armoured Cable. | Rmt | RO
| End Termination | Nos | RO
2.06 | 3.5C x 150 Sq.mm Aluminium XLPE Armoured Cable. | Rmt | RO
| End Termination | Nos | RO
2.07 | 3.5C x 120 Sq.mm Aluminium XLPE Armoured Cable. | Rmt | RO
| End Termination | Nos | RO
2.08 | 3.5C x 95 Sq.mm Aluminium XLPE Armoured Cable. | Rmt | RO
| End Termination | Nos | RO
2.09 | 3.5C x 70 Sq.mm Aluminium XLPE Armoured Cable. | Rmt | RO
| End Termination | Nos | RO
2.1 | 3.5C x 50 Sq.mm Aluminium XLPE Armoured Cable. | Rmt | RO
| End Termination | Nos | RO
2.11 | 3.5C x 35 Sq.mm Aluminium XLPE Armoured Cable. | Rmt | 40 |  |  | 0 | 0
| End Termination | Nos | 2 |  |  | 0 | 0
2.12 | 4C x 25 Sq.mm Aluminium XLPE Armoured Cable. | Rmt | RO
| End Termination | Nos | RO
LT Control Cables
Screened shielded steel armoured copper conductor control cables. Supply, laying, end termination, testing and commissioning of screened shielded armoured copper conductor cable. The cable shall be laid in existing Cable tray/ hume pipe / trench. The rate quoted excludes the cost of Cable tray/ hume pipe/ trench.
Tentative quantities have been considered. Final quantities to be as per Vendor Control cable schedule.
2.13 | 19C x 2.5 sqmm Armoured copper conductor cable | Rmt | RO
| End Termination | Nos | RO
2.14 | 10C x 2.5 sqmm Armoured copper conductor cable | Rmt | RO
| End Termination | Nos | RO
2.15 | 4C x 2.5 sqmm Armoured copper conductor cable. | Rmt | RO
| End Termination | Nos | RO
2.16 | 3C x 2.5 sqmm Armoured copper conductor cable. | Rmt | 20 |  |  | 0 | 0
| End Termination | Nos | 4 |  |  | 0 | 0
2.17 | 2C x 2.5 Sq.mm Copper PVC Unarmoured Cable. | Rmt | 50 |  |  | 0 | 0
| End Termination | Nos | 4 |  |  | 0 | 0
| SUB TOTAL |  |  |  |  | 0 | 0
3 | SECTION III - Earth Electrodes and Earth Strips
A | EARTH ELECTRODES
Body earthing
3.01 | Supply, earth excavation, back filling, chamber and fixing of 100mm DIA GI Pipe earth station in conformity with IS 3043. 2 no's of 50x6 GI strip, CI funnel of 20 gauge, block masonry chamber of 450mm(L)x 450mm(B)x 300mm(H) (clear space), concrete base CI Man hole cover with frame painted with bitumastic paint and packing with mixture of charcoal and salt around the pipe electrode including digging upto permanent water level but not less than 3mtr back filling as required. The earth resistance shall be less than 4 ohms. All work shall be carried out in conformity with specifications, standards & Codes. Refer Single line diagram, earthing schematic diagram and fault level calculations. Rate Shall include the labelling of the earth pits as per project manager's instructions. | Nos | 6 |  |  | 0 | 0
Neutral earthing
3.02 | Supply, earth excavation, back filling, chamber and fixing of 0.6m x 0.6m x 4mm CU Plate earth station in conformity with IS 3043. 2 no's of 50x6 Cu strip, CI funnel of 20 gauge, block masonry chamber of 450mm (L)x 450mm(B) x 300mm(H) (clear space), concrete base CI Man hole cover with frame painted with bitumastic paint and packing with mixture of charcoal and salt around the plate electrode including digging upto permanent moisture level but not less than 3mtr back filling as required. The earth resistance shall be less than 4 ohms. All work shall be carried out in conformity with specifications, standards & Codes. Refer Single line diagram, earthing schematic diagram and fault level calculations. Rate Shall include the labelling of the earth pits as per project manager's instructions. | Nos | 4 |  |  | 0 | 0
Maintenance Free Earthing
3.03 | Supply, installation, testing & commissioning of MAINTENANCE FREE chemical earthing system in 150mm dia 3mtr bore hole with Single Earthing Electrode consist of 3mtr long 25m mm dia Copper earth electrode, Brass clamp terminal flat of 175 x 50 x 3 mm , the entire construction processed with Hot Dip Galvanization, outer surface up to 250-300 microns. The entire bore area shall be filled with highly conductive and non-corrosive nature crystalline material, along with electrode Moisture Booster compound of 3 x 25 Kg bags to fill surround the electrode at the time of installation or equivalent maintenance free earthing. (Moisture Booster having its property of moisture retention, conduction and non-corrosive nature). The cost shall include RCC chamber & CI cover. The resistance to be measured & witnessed by the client/consultant less than 1 ohm. The cost of Boring 150mm dia 3mtr long in hard rock area to be considered in the installation scope. For All equipment earthing | Nos | RO
B | EARTH STRIPS
Supply, laying, testing and commissioning of following sizes of GI/Cu earth continuity conductor (strips/ stranded wires) for interconnection between the earthing stations, panels, DB's & equipments etc on walls/ceiling, Corrosion protection for buried, Joints, conductors with bituminous coating and covered with PVC tapes etc all in conformity with the specifications as required, approved and directed. Note : Earth Strips laid in earth shall have sleeves. The rate shall include cost of laying Earth strip in floor with PVC sleeves. Rate shall include wall / floor chasing, rough plastering, clamping, Sleeve including End termination for Cables.
3.04 | 50 x 10 mm Hot dip galvanised GI strips | Rmt | RO
3.05 | 50 x 6 mm Hot dip galvanised GI strips | Rmt | 100 |  |  | 0 | 0
3.06 | 40 x 10 mm Hot dip galvanised GI strips | Rmt | RO
3.07 | 40 x 6 mm Hot dip galvanised GI strips | Rmt | RO
3.08 | 25 x 6 mm Hot dip galvanised GI strips | Rmt | RO
3.09 | 25 x 3 mm Hot dip galvanised GI strips | Rmt | RO
3.1 | 40 x 6 mm CU strips | Rmt | RO
3.11 | 25mm x 6mm CU strips | Rmt | 60 |  |  | 0 | 0
3.12 | 25mm x 3mm CU strips | Rmt | RO
3.13 | 1C x 10 Sqmm Copper Earting Cable | Rmt | RO
3.14 | 1C x 6 Sqmm Copper Earting Cable | Rmt | RO
3.15 | 1C x 4 Sqmm Copper Earting Cable | Rmt | RO
3.16 | 1C x 2.5 Sqmm Copper Earting Cable | Rmt | RO
3.17 | Busbar of 0.5 Mtr length made out of 25x6 mm CU strip with drill holes of M8 at 25mm interval mounted on insulators. | Nos | RO
3.18 | Busbar of 0.5 Mtr length made out of 50x10 mm GI strip with drill holes of M8 at 25mm interval mounted on insulators. | Nos | RO
| SUB TOTAL |  |  |  |  | 0 | 0
4 | SECTION IV : DG
4.01 | Supply of 415 V, 3 Ph. 1500 RPM, 500 KVA Standby operated & rated diesel generating set with Acoustic Enclosure along with Radiator type of cooling arrangement and associated accessories including, Stack,Starting Batteries, AVM Pads, Suitable Silencer and Manual Control Panel, etc., | No. | RO
4.02 | Steel work as required to support the exhaust system 15M Height. Related civil works shall be as per approved drawing and specifications. | Kgs | RO
Note : Vendor shall study the DG set layout and routing of flue gas exhaust pipe and suggest suitable size of ERW "B" class pipe and bends to achieve free flow of flue gas without developing any back pressure on turbocharger, size of the pipe shall be supported by back pressure design calculations. Individual exhaust system shall be provided.
| SUB TOTAL |  |  |  |  | 0 | 0
5 | SECTION V - Miscellaneous items.
5.01 | supply and installation Shock treatment chart with teak wood frame and glass cover as approved | Nos | RO
5.02 | supply and installtion Rubber mat 1100V grade ISI approved, size- 1.8 m x 0.9m | Nos | RO
5.03 | supply and installation First aid kit | Nos | RO
5.04 | supply and installtion Laminated Schematic with glass frame | Nos | RO
5.05 | supply and installtion LT tool kit. | Nos | RO
5.06 | 6mm thick MS chequered plates with 2 coats of primer and final enamel paint for electrical shaft. The Cost shall include MS support required for supporting Checker plate. | Kgs | 200 |  |  | 0 | 0
5.07 | Supplying and laying of R.C.C NP2 class Hume pipe laid to the required level and grade with collars joining in CM 1:3, Cost to invclude Excavation and filling the excavated area with approved quality soil on sides, bottom and top surface of pipe with all leads and lifts, making necessary connections as required etc.,complete.
5.08 | 300 mm Dia RCC Hume pipe | Rmt | 20 |  |  | 0 | 0
5.09 | 200 mm Dia RCC Hume pipe | Rmt | RO
5.1 | 150 mm Dia RCC Hume pipe | Rmt | 10 |  |  | 0 | 0
5.11 | Supply and laying of heavy duty 100mm Dia HDPE pipe for road crossing. Cost to invclude Excavation and filling the excavated area with approved quality soil on sides, bottom and top surface of pipe with all leads and lifts, making necessary connections as required etc.,complete. | Rmt | RO
5.12 | Supply and laying of heavy duty 50mm Dia HDPE pipe for road crossing. Cost to invclude Excavation and filling the excavated area with approved quality soil on sides, bottom and top surface of pipe with all leads and lifts, making necessary connections as required etc.,complete. | Rmt | RO
5.13 | Supply and laying of heavy duty 32mm Dia HDPE pipe for road crossing. Cost to invclude Excavation and filling the excavated area with approved quality soil on sides, bottom and top surface of pipe with all leads and lifts, making necessary connections as required etc.,complete. | Rmt | RO
CEIG
5.14 | Professional charges towards filing application, following & arranging approval of drawings / scheme of both external and internal works by Electrical Inspectorate, obtaining clearance from Electrical Inspectorate for the installation & commissioning of entire electrical works arranging service of the installation including necessary charges to be paid towards approval. | GRO | RO
Construction of RCC pull chamber of M20grade of size mentioned below with 150mm thick walls and 125mm thick bottom slab/top slab, including the cost of 75mm thk PCC 1:2:4, Shuttering, cost of Reinforcement steel, curing, internal walls plastered smooth in CM 1:3 and external walls plastered in 1:6 with sponge finish, backfilling, ramming, removal of surplus soil with all leads and lifts, materials, labour, transportation etc., complete. Supply and Fixing RCC heavy duty Cover with frame and grating up to 20 tons on top surface flushed to the finished floor level with necessary excavation, back filling the selected excavated earth with all leads and lifts etc., complete.
5.15 | 1.0M x 1.0M x 1.2M Cable Pull Chamber with Cover | Nos | 2 |  |  | 0 | 0
5.16 | 0.75M x 0.75M x 0.75M Cable Pull Chamber with Cover | Nos | RO
5.17 | 0.6M x 0.6M x 0.9M Cable Pull Chamber with Cover | Nos | RO
| SUB TOTAL |  |  |  |  | 0 | 0
6 | SECTION VI : Foundation Works CIVIL RELATED ELECTRICAL WORKS
6.01 | Construction of RCC foundation for Transformer as per the drawing | Cum | RO
Note: 1. The contractor must check the existing RCC foundation. 2. If the existing RCC foundation is sufficient for the new requirements, no additional foundation is needed. 3. If the existing foundation is not sufficient, a new RCC foundation should be constructed as per the new requirements.
6.02 | Construction of RCC foundation for DG as per the drawing | Cum | 5
6.03 | Construction of RCC foundation for DG Stack as per the drawing | Cum | 2
| SUB TOTAL |  |  |  |  | 0 | 0
| GRAND TOTAL EXCLUDING GST |  |  |  |  | 0 | 0

## SECTION II-LT PANELS
PROJECT | : NATIONAL LAW SCHOOL OF INDIA UNIVERSITY, BENGALURU
CONSULTANTS | : LEAD CONSULTANCY & ENGINEERING SERVICES (INDIA) PVT. LTD
SUBJECT | : SUMMARY FOR LT PANELS
REV NO | : R1
DATE | 06.03.2025
GENERAL NOTES
Note 1 | Unless specified all works are for Design, Manufacture, fabrication, loading , unloading, delivery, supply, installation, testing and commissioning to be considered by the panel supplier.
Note 2 | All bill of quantities items are to be read in conjunction with drawings and technical specifications whether specified or not.
Note 3 | Selection of all switchgear components - it is intended to achieve total discrimination and coordination, as such vendor shall justify selection of switchgear from upstream to final circuit components. The Vendor/Fabricator shall understand this from switchgear manufacturer before concluding selection.
Note 4 | Parallel to Annexure Vendor to Refer Single line diagram for details.
Note 5 | Vendors shall submit the technical data sheet duly filled.
ITEM NO | WORK DESCRIPTION | UNIT | QUANTITY | RATES (IN INR) |  | TOTAL RATES (IN INR)
|  |  |  | SUPPLY | INSTALLATION | SUPPLY | INSTALLATION
SECTION II - LT PANELS
1 | LT PANELS
PANEL FABRICATION DETAILS:
The cost of panels shall include cost of Supply, installation, commissioning, transportation, safely unloading & installation in identified location. delivered to site.
The fabrication shall be made up of CRCA sheet with thickness of 3mm frame, 2.0mm front door with components, 1.6mm all other partition.
The surface shall be rigorously treated for derusting in 9 tank process with dephosphating and painting with at least 2 coats of approved paint. The panel shall be totally metal clad type with double gasketting with rubber / resin lining enclosed.
The panel shall be mounted on trench and shall have cable entry provision from the top and bottom with suitable alley as the case may be.
The panel shall be tested for the same KA rating of the relevant highest rating ACB / MCCB.
All components shall be from ISO-9001 companies and shall have relevant IS/IEC approvals without fail. (Fabrication, drawing and list of components and panel detail shall be got approved by consultants before fabrication).
All Panels shall compliance to IEC -61403 fully type tested with internal ARC test.
The panel shall be fully interlocked as required.
The panel shall include base frame channel support of 75x40x6mm thk. (The Single Line Diagram may be closely be followed).
Note:-
1 | The Panel shall be fully as per the requirement of Electrical Inspectorate/ CEIG authorities.
2 | Auxiliary contactor to be provided along with auto-manual switch where ever required.
3 | All Breakers both Incoming & Outgoing shall have LED 'ON / OFF / TRIP' indications whether mentioned in as per SLD or Not.
4 | CTs shall be with single / dual ratio as per SLD and cast resin type only.
5 | ACBs earthing shall be carried out with Cu. Bus.
6 | Incoming Feeders will have potential free spare contacts for ON/OFF/TRIP status indication for third party BMS in all Panels.
7 | All starter feeder shall have potential free spare contacts for A/M, ON/OFF, TRIP status indication for third party BMS in all Panels.
8 | For Capacitors earthing shall be provided.
9 | Ventilators with necessary fans shall be provided for Panels liberally with mesh for Capacitor Panels.
10 | Dedicated Ventilation fan shall be provided for VFD feeder in each compartment shall ON when VFD starts & shall OFF with Delay of 1 Minute after VFD is switched off.
11 | Al. earthing shall be provided for all panels as per short circuit.
12 | All ACBs shall confirm IS 13947-1/IEC 947-1 for general rules & IS 13947 rules & IS 13947-2/IEC 947-2 for Circuit breakers.
13 | All doors to have double rubber gasket with shutter assembly & door seating frame.
14 | Any panel if more than 1.2mts width, compartment should be made in parts each part not exceeding 1.2 mts or even lesser is acceptable .
15 | The current density for ALU busbars shall be 0.8 A/Sqmm for all panels.
16 | The current density for CU busbars shall be 1.2 A/Sqmm only.
17 | All UPS outgoing panels shall have neutral busbars double the size of phase.
18 | Insulation level shall be 2.5 KV / 1 Min.
19 | TP means three pole.
20 | TPN means 4 pole breaker with 50% neutral
21 | 4P means Four Pole breaker with 100% neutral
22 | The degree of ingress protection of indoor panels shall be IP 52.
23 | All breakers to have breaker manufacturer's factory made Spreaders.
24 | In any case Aluminium / copper bus bars should not be connected directly to the breaker without spreaders.
25 | The control wiring has to be in Troughs of appropriate size.
26 | Irrespective of the Ampacity all breakers shall be connected to the breakers using Bus bars only. Only Uninyvin Cables in special cases shall be accepted.
27 | All vertical bus bars in bus bar alley shall have bottom supports.
28 | Panel earthing strip should come out vertically on top of the panel.
29 | Ics should be 100% Icu for service voltage. Any other percentage shall not be accepted.
30 | The Bus bars and connectors should have extruded insulation.
31 | Door earthings shall be provided for all doors using braided copper.
32 | Base frame shall be with each panel. The size will be equal to each section.
33 | Bi-metallic tape / washers to be used where ever copper & Aluminium bus bar are joined.
34 | All incomers & chillers feeders as per single line diagram
35 | All test certificates shall be provided immediately after testing & commissioning.
36 | Potential free contacts in all the panels must be provided on all Breakers - (ON / OFF, Trip) wired upto the common terminal block .
37 | All Energy meters must have RS 485 port and looped internally and wired upto the common terminal block for hooking to third party BMS.
38 | Auto-Manual switch shall be provided for all motorised breakers.
39 | Maximum Operating height of the panel shall be of 1800mm from FFL Minimum Operating height of the panel shall be of 350mm from FFL.
40 | All LT panels will be tested and inspected by client for manufacture process and quality at manufacturers works before dispatching the products to site.
41 | The Controls MCBs shall be of 6A.
42 | All ACB and MCCB to be of compact type as per make list.
43 | MCCB breakers to be provided with Rotary Handle along extended shaft.
44 | The terminal block used in LV switchgear , MCCs, DBs should have fully finger touch proof construction.
45 | Form of Construction shall be 4A for the main panels and 3B for all other panels.
46 | Wherever the PLC is applicable, the vendor / contractor has to make sure that panel is delivered along with the PLC. No additional cost will be entertained after the delivery of panels.
47 | Approval shall be taken for each & every panel including all interlocking schemes proposed in the form of Shop Drawings before fabrication.
48 | The Panel nomenclature (Engraved Metal Labels) Shall be strictly as per SLD & BOQ.
49 | Electrical panel vendor shall ensure sufficient size to be provided for active harmonic filter outgoing feeder. If rating of active harmonic filter is not finalised at the time panel approval, panel vendor shall provide one step higher size compartment size for allocating respective feeder.
50 | Electrical panel vendor shall ensure sufficient size Neutral busbar sizes to be provided for connection Active harmonic filter as per Active harmonics vendor recommendations.
50 | Electrical panel vendor shall ensure sufficient size Neutral busbar sizes to be provided for connection Active harmonic filter as per Active harmonics vendor recommendations.
1.1 | EB & DG CHANGEOVER PANEL IP-55 OUTDOOR PANEL | No. | 1 |  |  | 0 | 0
| TOTAL FOR LT PANELS |  |  |  |  | 0 | 0