## RO PLANT
PROJECT : JSW ACADEMIC BLOCK - NLSIU
MEP CONSULATNT : LEAD CONSULTANCY & ENGINEERING SERVICES PVT. LTD.
SUBJECT : BILL OF QUANTITIES FOR RO PLANT WORKS
SL.NO | DESCRIPTION | UNIT | QUANTITY | RATE IN (INR) |  | TOTAL SUPPLY AMOUNT IN (INR) |  | REMARKS
|  |  |  | SUPPLY | INSTALLATION | SUPPLY | INSTALLATION
RO PLANT- 500 LPH
1 | Design, Supply, Installation, Testing and Commissioning of Reverse Osmosis (RO) Water treatment Plant (500 LPH - Treated Water Flow Rate) of required Capacities as mentioned :- The system Should be comprising of the following
2 | Outlet Water Quality Parameters :- Potable water as per IS 10500 : 2012. RO Plant the TDS Less than or equal to 50 ppm.
3 | Raw water feed pump to filtration plant & RO Feed Pump. The pumps shall be Centrifugal multistage vertical/Horizontal inline pump with all required accessories suitable for water applications. The motor should be 3 Phase 415 V, 50 Hz along with foundation bolts. The head and the flow rate is 1 Lps at 35M head (1W+1S) | Set | 1 |  |  | 0 | 0
4 | Inline Hypo Dosing System inclusive of electrical diaphragm metering pump with accessories such as foot valve, dosing valve, level switch and the MOC of wet parts to be PP/PVC. System to be complete with LLDPE tank minimum 100 Ltrs. with PVC flexible hose supporting flow rate of min. 5 LPH | Each | R0
5 | Multigrade Sand Filter Manual Down Flow type of MOC as FRP complete with a multiport valve with PVC frontal maximum working pressure of 3.5 kg/cm². Internal media complete with mixture of multi grade sand and support media. | Each | 1 |  |  | 0 | 0
6 | Activated Carbon Filter Manual Down Flow type of MOC as FRP complete with a multiport valve with PVC frontal maximum working pressure of 3.5 kg/cm². Internal media comprising of activated carbon with support media. | Each | 1 |  |  | 0 | 0
7 | High Pressure Pump for RO System The pumps shall be Centrifugal multistage vertical inline pump with all required accessories suitable for water applications. The motor should be 3 Phase 415 V, 50 Hz along with foundation bolts. The head and the flow rate is 1 Lps at 35M head (1W+1S) | Set | 1 |  |  | 0 | 0
8 | Skid Mounted RO System with maximum recovery possible with vertical membrane assembly with the inlet, outlet & reject plumbing - 2 Membrane system | Each | 1 |  |  | 0 | 0
9 | Instrumentation & Control Panel for each Prefiltration, RO water treatment Plant with a provision of electrical supply to the various equipments with an inbuilt Logic controllers to maintain plant operations. It should be complete with an visual annunciation panel to monitor the plant operation and status. It should be comprising of a timer for auto flush and safety interlocks. The offer should be complete with a level switches and their associated cabling, accessories with mounting arrangement for the HDPE treated water tanks. The RO Plant On/Off operations to be modulated by the Level Switches. The electrical panel should be comprising of the potential free contacts for monitoring the RO Plant status. Complete with all required electrical components which required for proper functioning of the plant. Including Cabling Lot as required to complete the functionality. Plant Accessories such as Pressure Gauges, Flow Indicators, Isolation Valves (Butterfly and Ball Valves), Interconnecting CPVC piping, Water Meters, etc. complete with all required fittings and accessories for satisfactory functioning of the RO Plant RO Plant should be complete with a provision for a Cleaning system of RO membranes with required equipments and accessories. | Each | 1 |  |  | 0 | 0
| SS Tank: 1000 L | Each | 2 |  |  | 0 | 0
10 | Cost shall be inclusive of rejected water piping (Minimum 3m) till the discharge point and interconnecting piping within the plant [Reject water plumbing is considered for 10 Meters] | 1 lot |  |  |  | 0
| T O T A L |  |  |  |  | 0 | 0
GST @ 18% | [5 empty] | 0
GRAND TOTAL INCL GST | [5 empty] | 0